## ESS Metron Proposal XXXXXX

| DATE: | SUBJECT: |
| --- | --- |
| TO: | FROM: |
| ATTN: | REFERENCE: |

ESS Metron is pleased to offer the following proposal:

### ITEM #1: Generator GEN-MSG Switchboard                                                    $XX,XXX.00

### ITEM #2: Main MAIN-MSG Switchboard                                                          $XX,XXX.00

### ITEM #3: Panel-M Switchboard                                                                           $XX,XXX.00

### ITEM #1: Generator GEN-MSG Switchboard:

Electrical Rating:

- 1600A, 600VAC, 3phs, 4wire, 22Kaic

- Service Entrance Label

- 1600Amp  Plated Copper Main Bus

General Enclosure Information All Sections Combined:

- Qty  vertical sections, , Floor Mount

- Total Switchboard Approx Dim 90”T x 74”W x 24”D

- Switchboard material -

- Finish -

- Color -

- Rear access required -

- Labels -

- Ground bar extending through all sections

- Main cross bus to be epoxy coated

- Main cross bus splices with boots

Sectional Information:

Section 1: - UL Listed and Marked  - 90”T x 30”W x 24”D

- Qty (1) circuit breaker “MAIN”: 1600AF/1600AT, 600VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 1600A rating plug

  - LSIG trip unit

  - Neutral current sensor

  - (6) #2-600MCM  lugs per phase and neutral

- Qty (1) Copper Ground Bar with  (2)  lugs

- Set of copper bus, splices, hardware, and bracing to connect the horizontal cross bus and ground bar between sections

Section 2: - UL Listed and Marked  - 90”T x 44”W x 24”D

- Qty (1) 1200 Amp Group mounted interior, 22Kaic, center tapped, 100% rated, with the following:

  - Copper bus

  - Feeder breakers:

    - Qty (2) - 600AF/500AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 1200AT/800AT, 3 pole, electronic LSI trip, 800A rating plug, mechanical lugs

- Qty (1) Control Power Transformer, 480-120V Pri/Sec fused

- (1) lot section heaters with thermostat

- Qty (1) Copper Ground Bar with  (2)  lugs

### ITEM #2: Main MAIN-MSG Switchboard:

Electrical Rating:

- 1200A, 480/277VAC, 3phs, 4wire, 22Kaic

- Service Entrance Label

- 1200Amp  Plated Copper Main Bus

General Enclosure Information All Sections Combined:

- Qty  vertical sections, , Floor Mount

- Total Switchboard Approx Dim 90”T x 104”W x 24”D

- Switchboard material -

- Finish -

- Color -

- Rear access required -

- Labels -

- Ground bar extending through all sections

- Main cross bus to be epoxy coated

- Main cross bus splices with boots

Sectional Information:

Section 1: - UL Listed and Marked  - 90”T x 44”W x 24”D

- Qty (1) 1200 Amp Group mounted interior, 22Kaic, center tapped, 100% rated, with the following:

  - Copper bus

  - Feeder breakers:

    - Qty (1) - 30AF/20AT, 1 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 150AF/20AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 150AF/40AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 150AF/70AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 150AF/125AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 250AF/225AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (2) – 600AF/400AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 1200AF/1000AT, 3 pole, electronic LSI trip, mechanical lugs

- (1) lot section heaters with thermostat

- Qty (1) NEMA 4X filtered Fan Kit

- Qty (1) Copper Ground Bar with  (2)  lugs

- Set of copper bus, splices, hardware, and bracing to connect the horizontal cross bus and ground bar between sections

Section 2: - Main Section per EUSERC - UL Listed and Marked  - 90”T x 30”W x 24”D

- Qty (1) circuit breaker “MAIN”: 1200AF/1200AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 1200A rating plug

  - LSIG trip unit

  - Neutral current sensor

  - (6) #2-600MCM  lugs per phase and neutral

- Qty (1) Control Power Transformer, 480-120V Pri/Sec fused

- (1) lot section heaters with thermostat

- Qty (1) Ground fault relay

- Qty (1) Ground fault CT

- Qty (1) Utility metering socket and sealing ring

- (1) lot indicating lights

- Qty (1) Copper Ground Bar with  (2)  lugs

- Set of copper bus, splices, hardware, and bracing to connect the horizontal cross bus and ground bar between sections

Section 3: - UL Listed and Marked  - 90”T x 30”W x 24”D

- Qty (1) Utility pull section

- Qty (1) NEMA 4X filtered Fan Kit

- Qty (1) Copper Ground Bar with  (2)  lugs

- Set of copper bus, splices, hardware, and bracing to connect the horizontal cross bus and ground bar between sections

### ITEM #3: Distribution Panel-M Switchboard:

Electrical Rating:

- 1000A, 208/120VAC, 3phs, 4wire, 22Kaic

- Service Entrance Label

- 1000Amp  Plated Copper Main Bus

General Enclosure Information All Sections Combined:

- Qty  vertical sections, , Floor Mount

- Total Switchboard Approx Dim 90”T x 44”W x 24”D

- Switchboard material -

- Finish -

- Color -

- Rear access required -

- Labels -

- Ground bar extending through all sections

Sectional Information:

Section 1: - UL Listed and Marked  - 90”T x 44”W x 24”D

- Qty (1) 1000 Amp Group mounted interior, 22Kaic, center tapped, 100% rated, with the following:

  - Copper bus

  - Feeder breakers:

    - Qty (5) - 250AF/200AT, 3 pole, thermal magnetic trip, mechanical lugs

    - Qty (1) – 250AF, 3 pole, space

- (1) lot section heaters with thermostat

- Qty (1) Copper Ground Bar with  (2)  lugs

Exceptions/Clarifications:

Any deviation from the scope of this proposal may result in a cost adjustment

Breaker coordination studies by others

Neutral CT’s to be Rogowski type

Utility meter provided by others

Exception to insulated ground bus

Terms and Conditions:

COMMODITY METAL PRICE DISCLAIMER

Due to highly unstable commodity metal prices related to factors beyond our control, Metron is unable to hold its prices firm for longer than 90 days.  We are making every effort to minimize the impact of such variations and appreciate your understanding.  Orders placed later than 90 days after quotation are subject to a price revision based on most current metal commodity pricing.

Shipment:	Approval Drawings: 2-3 weeks

#### Manufacturing Lead Time, 6-8 weeks after release of approved dwgs

Terms:	N30

FOB: 	Metron Inc., Denver, Colorado, shipping prepaid and allowed.

Validity:	Prices Valid Thirty (30) Days From the Date of This Quotation