## ESS Metron Proposal XXXXXX

| DATE: | SUBJECT: |
| --- | --- |
| TO: | FROM: |
| ATTN: | REFERENCE: |

ESS Metron is pleased to offer the following proposal:

ITEM #1 – Qty (3) 600A Switchboard Lineups							$XXX,XXX.00

ITEM #2 – Option Qty (3) 600A Switchboard Lineups With Common Load Breaker			$XXX,XXX.00

### ITEM #1 - Main Paralleling Switchboard:

Electrical Rating:

- 600A, 480VAC, 3phs, 4wire, 65Kaic

- UL Listed and Marked

- Service Entrance Label

General Enclosure Information All Sections Combined:

- Qty (2) vertical sections, , Floor Mount

- Total Switchboard Approx Dim 90”T x 64”W x 60”D

- Switchboard material -

- Finish -

- Color -

- Hinged doors with thumb screw hardware for circuit breaker and control device compartments.

- Access covers sides and rear

- Rear access required -

Sectional Information:

Section 1:

- Qty (1) Circuit breaker “52-G1”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (1) Circuit breaker “52-G2”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (1) E-stop PB

- Qty (6) CT

- Qty (3) PT

- Qty (2) CPT

- Qty (1) Copper Ground Bar with  (2) #2/0  lugs

- Qty (2) Digital Generator Control Panel “EasYGen 2500” with the following features:

LCD displays for indication of generator electrical parameters, engine generator alarms, engine generator status and configuration parameters.

Section 2:

- Qty (1) Circuit breaker “52-G3”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (3) CT

- Qty (2) PT

- Qty (1) CPT

- Qty (1) Copper Ground Bar with  (2) #2/0  lugs

- Qty (1) Digital Generator Control Panel “EasYGen 2500” with the following features:

LCD displays for indication of generator electrical parameters, engine generator alarms, engine generator status and configuration parameters.

- Qty (1) Common load bus with  (6) #2-600MCM Mechanical lugs per phase and neutral

ITEM #2 - Main Paralleling Switchboard With Common Load Breaker:

Electrical Rating:

- 600A, 480VAC, 3phs, 4wire, 65Kaic

- UL Listed and Marked

- Service Entrance Label

General Enclosure Information All Sections Combined:

- Qty (2) vertical sections, , Floor Mount

- Total Switchboard Approx Dim 90”T x 64”W x 60”D

- Switchboard material -

- Finish -

- Color -

- Hinged doors with thumb screw hardware for circuit breaker and control device compartments.

- Access covers sides and rear

- Rear access required -

Sectional Information:

Section 1:

- Qty (1) Circuit breaker “52-G1”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (1) Circuit breaker “52-G2”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (1) E-stop PB

- Qty (6) CT

- Qty (3) PT

- Qty (2) CPT

- Qty (1) Copper Ground Bar with  (2) #2/0  lugs

- Qty (2) Digital Generator Control Panel “EasYGen 2500” with the following features:

LCD displays for indication of generator electrical parameters, engine generator alarms, engine generator status and configuration parameters.

Section 2:

- Qty (1) Circuit breaker “52-G3”: 800AF/150AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 200A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (2) Mechanical lugs per phase

- Qty (1) Circuit breaker “LOAD”: 800AF/300AT, 480VAC, 65kAIC, 3pole, , , 100% rated, with the following accessories:

  - 300A rating plug

  - LSIG trip unit

  - Neutral CT

  - 120VAC Motor Operators

  - 120VAC Close Coil

  - 24VDC Shunt Trip

  - Bell  Alarm w/aux contacts

  - (4) Aux contacts

  - Manual Close pushbutton cover

  - (6) #2-600MCM Mechanical lugs per phase

- Qty (3) CT

- Qty (2) PT

- Qty (1) CPT

- Qty (1) Copper Ground Bar with  (2) #2/0  lugs

- Qty (1) Digital Generator Control Panel “EasYGen 2500” with the following features:

LCD displays for indication of generator electrical parameters, engine generator alarms, engine generator status and configuration parameters.

Clairifications/Exceptions:

- Onsite startup assistance not included in this proposal – will be provided by others

- Breaker trip coordination provided by others

- Any deviation from the scope in this proposal may result in a price adjustment

Terms and Conditions:

COMMODITY METAL PRICE DISCLAIMER

Due to highly unstable commodity metal prices related to factors beyond our control, Metron is unable to hold its prices firm for longer than 30 days.  We are making every effort to minimize the impact of such variations and appreciate your understanding.  Orders placed later than 30 days after quotation are subject to a price revision based on most current metal commodity pricing.

Shipment:	Approval Drawing Lead Time 1-2 weeks

Manufacturing Lead Time 6-8 weeks.

Terms:	Net 30 days with Approved Credit

FOB: 	Metron Inc., Denver, Colorado, customer is responsible for all freight charges

Validity:	Prices Valid Thirty (30) Days from the Date of This Quotation